## DESIGN 1
[9 empty] | Assuming 500 MW |  |  |  | Turbine eff
|  | S.P | P (Mpa) | T © | H (Kj/Kg) | V (m3/kg) | S (kJ/kgK) | m (kg) | ms (kg/s) |  |  |  | 0.49 |  |  |  |  | SCRATCH SECTION
| BOILER | 1 | 20 | 540 | 3363.5 | - | 6.2982 | 1 | 664.9221 |  |  |  | Pactual (Mpa) | Tactual (oC) | hactual (Kj/kg)
interpolate using P and S | CFWH4 | 2 | 11.4 | 441.0918 | 3192.3663 | - | 6.2982 | 0.077265 | 51.3755 | SHV | P2a=P2-P2(0.07) | P2a | 10.602 | 315.3939 | 3279.6445
interpolate using P and S | RH | 3 | 10.2 | 422.9157 | 3160.9554 | - | 6.2982 | 0.92273 | 613.5467 | SHV
interpolate using P and S |  | 4 | 10.2 | 540 | 3473.7 | - | 6.7142 | 0.92273 | 613.5467 | SHV | [8 empty] | 1 |  | 1
interpolate using P and S | CFWH3 | 5 | 8 | 496.9753 | 3390.7685 | - | 6.7142 | 0.031708 | 21.0832 | SHV | P5a=P5-P5(0.07) | P5a | 7.44 | 290.038 | 3433.0636 |  |  |  | 2 |  | x
interpolate using P and S | DEAE | 6 | 5.8 | 442.9586 | 3287.5893 | - | 6.7142 | 0.037051 | 24.6361 | SHV | P6a=P6-P6(0.07) | P6a | 5.394 | 268.7692 | 3361.7812 |  |  |  | 3 |  | 3
interpolate using P and S | CFWH2 | 7 | 4.2 | 392.095 | 3191.107 | - | 6.7142 | 0.037756 | 25.1051 | SHV | P7a=P7-P7(0.07) | P7a | 3.906 | 249 | 3278.1508
interpolate using P and S | CFWH1 | 8 | 2.8 | 332.8021 | 3079.3129 | - | 6.7142 | 0.22053 | 146.6369 | SHV | P8a=P8-P8(0.07) | P8a | 2.604 | 226.1716 | 3180.7202 |  |  |  | x=
s9=sf+xsfg , h9=hf+xhfg | COND | 9 | 0.0055 | 34.58 | 2057.6146 | - | 6.7142 | 0.59569 | 396.0854 | SHV | P9a=P9-P9(0.07) | P9a | 0.005115 | 32.974 | 2630.3985
hf=h10 |  | 10 | 0.0055 | 34.58 | 144.95 | 1.0058 | - | 0.59569 | 396.0854
P at 2.8 Mpa |  | 11 | h10+Vf10(P11-P10) | 34.6686 | 147.7607 |  |  | 0.59569 | 396.0854 |  | Tactual = Tsat @ Pactual
| Table 2 | 12 | hf @ P8a | 226.1694 | 972.2296 |  |  | 0.25829 | 171.742 |  | hactual = hinlet - nturbine (hinlet - houlet)
| Table 2 | 13 | h14 | 226.1716 | 972.2397 |  |  | 0.25829 | 171.742
| Table 1 | 14 | hf @ T14 | 226.1716 | 972.2397 |  |  | 0.59569 | 396.0854 |  | TTD=2.3 |  | T14=T8a-TTD | 223.8716
| Table 2 | 15 | h14 | 226.1716 | 972.2397 |  |  | 0.85398 | 567.8274
| Table 2 | 16 | hf @ P7a | 249 | 1080.4856 |  |  | 0.037756 | 25.1051
| Table 1 | 17 | hf @ T17 | 246.7 | 1069.404 |  |  | 0.85398 | 567.8274 |  |  |  | T17=T7a-TTD | 246.7
| Table 2 | 18 | hf @ P6a | 268.7692 | 1178.2976 | 1.3353 |  | 1 | 664.9221
P at 20 Mpa, Vf18 at 1.335275 | Table 2 | 19 | h18+Vf18(P19-P18) | 273.192 | 1197.8006 |  |  | 1 | 664.9221
| Table 2 | 20 | hf @ P5a | 290.038 | 1289.262 |  |  | 0.10897 | 72.4586
| Table 1 | 21 | hf @ T21 | 287.738 | 1276.9083 |  |  | 1 | 664.9221 |  |  |  | T21=T5a-TTD | 287.738
| Table 2 | 22 | hf @ P2a | 315.3939 | 1433.3444 |  |  | 0.077265 | 51.3755
| Table 1 | 23 | hf @ T23 | 313.0939 | 1419.5634 |  |  | 1 | 664.9221 |  |  |  | T23=T2a-TTD | 313.0939
|  | SET VALUES | [15 empty] | p5 | 10 | 33.1887 | @ | p6 | 7
|  | GIVEN CASE 1 |  |  | at Pt. 9 | [12 empty] | p5 | 8 | 33.2048 | @ | p6 | 7
|  | FORMULA |  |  | x | 0.79049
|  | MANIPULATED | [13 empty] | EFFICIENCY
[18 empty] | p5 | 8 | 33.3213 | @ | p6 | 5.8
|  | MASS BALANCE | [15 empty] | p5 | 8 | 33.3042 | @ | p6 | 6
33.6825
FOR BOILER
|  | m1 (kg) | 1 |  | mblow = nblow(mwater) | 0.012
|  | nblowdown | 0.6 |  | mloss = nloss(mwater) | 0.008 | [11 empty] | p5 | 8 |  |  | p6 | 5.8 | p7 | 4.2
|  | nloss | 0.4 |  | m23 = mb + m1 + ml | 1.02 | [11 empty] | p5 | 8 | 33.7005 |  | p6 | 5.8 | p7 | 4.4
|  | mwater (kg) | 0.02
|  | FOR CFWH 4 |  |  | FOR DEAERATOR |  |  |  |  | FOR CHWH 2 |  |  |  | FOR COND
|  | m2h2a+m21h21=m22h22+m23h23 |  |  | m6h6+m17h17+m20h20=m18h18 |  |  |  |  | m7h7a+m15h15=m16h16+m17h17 |  |  |  | m9=m10=m11
|  | m23, m21 | 1 | kg | m18=m20+m6+m17 |  |  |  |  | m15=m17 |  |  |  | m9, m10 | 0.59569
|  | m2=m22 |  |  | m17=m23-m2-m5-m6 | 0.89103 | minus m6 |  |  | m16=m7
|  | m2, m22 | 0.077265 | kg | m6 | 0.037051 |  |  |  | m15 | 0.85398 | [7 empty] | H | Pactual | Tacrual | hactual
|  | FOE CFWH 3 |  |  | m17 | 0.85398 |  |  |  | m16, m7 | 0.037756 | [6 empty] | 10
|  | m22h22+m5h5a+m19h19=m21h21+m20h20 |  |  | m18 | 1 |  |  |  | FOR CHWH 1
|  | m20=m22+m5 | [7 empty] | m16h16+m8h8a+m11h11=m12h12+m14h14
|  | m19, m21 | 1 | kg | [5 empty] | m12=m16+m8
|  | m5 | 0.031708 | kg | [5 empty] | m11=m14
|  | m20 | 0.10897 | kg | [5 empty] | m11, m14 = m23-m2-m5-m6-m7-m8
[10 empty] | m11, m14 | 0.81622 | minus m8
[10 empty] | m8 | 0.22053
[10 empty] | m12 | 0.25829
[10 empty] | m11 | 0.59569
WORK TURBINE
|  | WT | m23(h1-h2a)+(m23-m2)(h2a-h3)+(m23-m2)(h4-h5a)+(m23-m2-mr5)(h5a-h6a)+(m23-m2-m5-m6)(h6a-h7a)+(m23-m2-m5-m6-m7)(h7a-h8a)+(m23-m2-m5-m6-m7-m8)(h8a-h9a)
|  | WT | 773.1477 | [13 empty] | KJ/Kg
SUMMARY
|  | WORK PUMP | [12 empty] | FOR TRUBINE WORK
[15 empty] | m1 | 1
[15 empty] | m23 | 1
|  | P1 | h11-h10 | 2.8107 | [10 empty] | m2 | 0.077265
|  | P2 | h13-h12 | 0.010056 | [10 empty] | m5 | 0.031708
|  | P3 | h19-h18 | 19.503 | [10 empty] | m6 | 0.037051
[15 empty] | m7 | 0.037756
|  | HEAT ADDED |  |  |  |  | CYCLE EFFICIENCY | [7 empty] | m8 | 0.22053
|  | QA | (h1-h23)+(m1-m2)(h4-h3)
|  | QA | 2232.5168 |  |  |  | n |  |  | (QA-QR)/QA |  |  |  |  | h1 | 3363.5
[7 empty] | n |  |  | 33.6825 |  |  |  |  | h2a | 3279.6445
|  | HEAT REJECTED | [12 empty] | h3 | 3160.9554
|  | QR | (m23-m2-m5-m6-m7-m8)(h9a-h10) |  |  |  | using turbine and pump | [7 empty] | h4 | 3473.7
|  | QR | 1480.5491 |  |  |  | n |  |  | Wt-Wp / Qa |  |  |  |  | h5a | 3433.0636
[10 empty] | 33.6313 |  |  |  |  | h6a | 3361.7812
|  | Wnet | 751.9678 | [11 empty] | h7a | 3278.1508
[15 empty] | h8a | 3180.7202
[15 empty] | h9a | 2630.3985

## DESIGN 2
[9 empty] | Assuming 500 MW |  |  |  | Turbine eff
|  | S.P | P (Mpa) | T © | H (Kj/Kg) | V (m3/kg) | S (kJ/kgK) | m (kg) | ms (kg/s) |  |  |  | 0.49 |  |  |  |  | SCRATCH SECTION
| BOILER | 1 | 20 | 540 | 3363.5 | - | 6.2982 | 1 | 654.576 |  |  |  | Pactual (Mpa) | Tactual (oC) | hactual (Kj/kg)
interpolate using P and S | CFWH5 | 2 | 11.4 | 441.0918 | 3192.3663 | - | 6.2982 | 0.077265 | 50.5761 | SHV | P2a=P2-P2(0.07) | P2a | 10.602 | 315.3939 | 3279.6445
interpolate using P and S | RH | 3 | 10.2 | 422.9157 | 3160.9554 | - | 6.2982 | 0.92273 | 603.9999 | SHV | Tactual = Tsat @ Pactual
interpolate using P and S |  | 4 | 10.2 | 540 | 3473.7 | - | 6.7142 | 0.92273 | 603.9999 | SHV | hactual = hinlet - nturbine (hinlet - houlet) | [7 empty] | 1 |  | 1
interpolate using P and S | CFWH4 | 5 | 8 | 496.9753 | 3390.7685 | - | 6.7142 | 0.031956 | 20.9173 | SHV | P5a=P5-P5(0.07) | P5a | 7.44 | 290.038 | 3433.0636 |  |  |  | 2 |  | x
interpolate using P and S | DEAE | 6 | 5.8 | 442.9586 | 3287.5893 | - | 6.7142 | 0.034529 | 22.6021 | SHV | P6a=P6-P6(0.07) | P6a | 5.394 | 268.7692 | 3361.7812 |  |  |  | 3 |  | 3
interpolate using P and S | CFWH3 | 7 | 4.3 | 395.6944 | 3197.9236 | - | 6.7142 | 0.0026096 | 1.7082 | SHV | P7a=P7-P7(0.07) | P7a | 3.999 | 250.3852 | 3281.491
interpolate using P and S | CFWH2 | 8 | 4.2 | 392.095 | 3191.107 | - | 6.7142 | 0.038568 | 25.2454 | SHV | P8a=P8-P8(0.07) | P8a | 3.906 | 249 | 3237.2028
interpolate using P and S | CFWH1 | 9 | 2.8 | 332.8021 | 3079.3129 | - | 6.7142 | 0.22162 | 145.0702 | SHV | P9a=P9-P9(0.07) | P9a | 2.604 | 226.1716 | 3159.8367 |  |  |  | x=
s10=sf+xsfg , h10=hf+xhfg | COND | 10 | 0.0055 | 34.58 | 2057.6146 | - | 6.7142 | 0.59345 | 388.4567 | SHV | P10a=P10-P10(0.07) | P10a | 0.005115 | 32.974 | 2619.7479
hf=h11 |  | 11 | 0.0055 | 34.58 | 144.95 | 1.0058 | - | 0.59345 | 388.4567
P at 2.8 Mpa |  | 12 | h11+Vf11(P12-P11) | 34.6686 | 147.7607 |  |  | 0.59345 | 388.4567 |  | TTD=2.3
| Table 2 | 13 | hf @ P9a | 226.1694 | 972.2296 |  |  | 0.2628 | 172.0238
| Table 1 | 14 | hf 15 | 226.1716 | 972.2397 |  |  | 0.2628 | 172.0238
| Table 1 | 15 | hf @ T15 | 226.1716 | 972.2397 |  |  | 0.59345 | 388.4567 |  |  |  | T15=T9a-TTD | 223.8716
| Table 1 | 16 | hf 15 | 226.1716 | 972.2397 |  |  | 0.85625 | 560.4805
| Table 2 | 17 | hf @ P8a | 249 | 1080.4856 |  |  | 0.041177 | 26.9536
| Table 1 | 18 | hf @ T18 | 246.7 | 1069.404 |  |  | 0.85625 | 560.4805 |  |  |  | T18=T8a-TTD | 246.7
| Table 2 | 19 | hf @ P7a | 250.3852 | 1087.2374 |  |  | 0.0026096 | 1.7082
| Table 1 | 20 | hf @ T20 | 248.0852 | 1076.0915 |  |  | 0.85625 | 560.4805 |  |  |  | T20=T7a-TTD | 248.0852
| Table 2 | 21 | hf @ P6a | 268.7692 | 1178.2976 | 1.2989 |  | 1 | 654.576
P at 20 Mpa, Vf21 |  | 22 | h21+Vf21(P22-P21) | 273.192 | 1197.2694 |  |  | 1 | 654.576
| Table 2 | 23 | hf @ P5a | 290.038 | 1289.262 |  |  | 0.10922 | 71.4934
| Table 1 | 24 | hf @ T24 | 287.738 | 1276.9083 |  |  | 1 | 654.576 |  |  |  | T24=T5a-TTD | 287.738
| Table 2 | 25 | hf @ P2a | 315.3907 | 1433.3444 |  |  | 0.077265 | 50.5761
| Table 1 | 26 | hf @ T26 | 313.0939 | 1419.5634 |  |  | 1 | 654.576 |  |  |  | T26=T2a-TTD | 313.0939
|  | SET VALUES | [15 empty] | p5 | 10 | 33.1887 | @ | p6 | 7
|  | GIVEN CASE 1 |  |  | at Pt. 9 | [12 empty] | p5 | 8 | 33.2048 | @ | p6 | 7
|  | FORMULA |  |  | x | 0.79049
|  | MANIPULATED | [13 empty] | EFFICIENCY
[18 empty] | p5 | 8 | 33.3213 | @ | p6 | 5.8
|  | MASS BALANCE | [15 empty] | p5 | 8 | 33.3042 | @ | p6 | 6
34.2149
|  | FOR BOILER | NOT INCLUDED
|  | m1 (kg) | 1 |  | mblow = nblow(mwater) | 0.012
|  | nblowdown | 0.6 |  | mloss = nloss(mwater) | 0.008 | [11 empty] | p5 | 8 |  |  | p6 | 5.8 | p7 | 4.2
|  | nloss | 0.4 |  | m23 = mb + m1 + ml | 1.02 | [11 empty] | p5 | 8 | 33.7005 |  | p6 | 5.8 | p7 | 4.4
|  | mwater (kg) | 0.02
|  | FOR CFWH 5 |  |  | FOR DEAERATOR |  |  |  |  | FOR CHWH 2 |  |  |  | FOR COND
|  | m2h2a+m24h24=m26h26+m25h25 |  |  | m6h6a+m23h23+m20h20=m21h21 |  |  |  |  | m8h8a+m16h16+m19h19=m18h18+m17h17 |  |  |  | m10=m11=m12
|  | m26, m24 | 1 | kg | m21=m23+m6+m20 |  |  |  |  | m17=m8+m19 |  |  |  | m10, m11 | 0.59345 | kg
|  | m2=m22 |  |  | m20=m26-m2-m5-m6 | 0.89078 | minus m6 |  |  | m16=m18
|  | m2, m25 | 0.077265 | kg | m6 | 0.034529 | kg |  |  | m17 | 0.041177 | kg | m8 | 0.038568 | kg |  |  |  | H | Pactual | Tacrual | hactual
|  | FOR CFWH 4 |  |  | m20 | 0.85625 | kg |  |  | m16, m18 | 0.85625 | kg | [5 empty] | 10
|  | m25h25+m5h5a+m22h22=m24h24+m23+h23 |  |  | m21 | 1 | kg |  |  | FOR CHWH 1
|  | m23=m25+m5 |  |  | FOR CFWH 3 |  |  |  |  | m17h17+m9h9a+m13h13=m12h12+m15h15
|  | m22, m24 | 1 | kg | m7h7a+m18h18=m20h20+m19h19 |  |  |  |  | m13=m17+m9
|  | m5 | 0.031956 | kg | m7 = m19 |  |  |  |  | m12=m15
|  | m23 | 0.10922 | kg | m20 = m18 |  |  |  |  | m12, m15 = m26-m2-m5-m6-m7-m8-m9
[5 empty] | m7 | 0.0026096 | kg |  |  | m12, m15 | 0.81507 | minus m9
[10 empty] | m9 | 0.22162 |  | kg
[10 empty] | m13 | 0.2628 |  | kg
[10 empty] | m12 | 0.59345 |  | kg
WORK TURBINE
|  | WT | m23(h1-h2a)+(m23-m2)(h2a-h3)+(m23-m2)(h4-h5a)+(m23-m2-mr5)(h5a-h6a)+(m23-m2-m5-m6)(h6a-h7a)+(m23-m2-m5-m6-m7)(h7a-h8a)+(m23-m2-m5-m6-m7-m8)(h8a-h9a)
|  | WT | [14 empty] | KJ/Kg
SUMMARY
|  | WORK PUMP | [12 empty] | FOR TRUBINE WORK
[15 empty] | m1 | 1
[15 empty] | m23 | 1
|  | P1 | [12 empty] | m2 | 0.077265
|  | P2 | [12 empty] | m5 | 0.031956
|  | P3 | [12 empty] | m6 | 0.034529
[15 empty] | m7 | 0.85625
|  | HEAT ADDED |  |  |  |  | CYCLE EFFICIENCY | [7 empty] | m8 | 0.22162
|  | QA | (h1-h26)+(m1-m2)(h4-h3)
|  | QA | 2232.5168 |  |  |  | n |  |  | (QA-QR)/QA |  |  |  |  | h1 | 3363.5
[7 empty] | n |  |  | 34.2149 |  |  |  |  | h2a | 3279.6445
|  | HEAT REJECTED | [12 empty] | h3 | 3160.9554
|  | QR | (m26-m2-m5-m6-m7-m8-m9)(h10a-h11) |  |  |  | using turbine and pump | [7 empty] | h4 | 3473.7
|  | QR | 1468.6636 |  |  |  | n |  |  | Wt-Wp / Qa |  |  |  |  | h5a | 3433.0636
[10 empty] | 0 |  |  |  |  | h6a | 3361.7812
[15 empty] | h7a | 3237.2028
|  | Wnet | 763.8533 | [11 empty] | h8a | 3159.8367
[15 empty] | h9a | 2619.7479

## DESIGN 3
| S.P | P (MPa) | T (C) | h (kJ/kg) | vf | S (kJ/kg-K) | m(kg) | m(kg/s) | Turbine eff | 0.49
Boiler | 1 | 20 | 540 | 3363.5 | _ | 6.2982 | 1 | 646.4122 |  |  | P-actual (Mpa) |  | T-actual (C) |  | h-actual (kJ/kg)
CFWH7 | 2 | 12 | 449.6117 | 3207.0544 | _ | 6.2982 | 0.013203 | 8.5347 | P2a= P2-P2(0.07) | P2a | 11.16 | T2a | 319.23 | h2a | 3286.8416
CFWH6 | 3 | 11.4 | 441.0918 | 3192.3663 | _ | 6.2982 | 0.078766 | 50.9153 | P3a= P3-P3(0.07) | P3a | 10.602 | T3a | 315.3939 | h3a | 3240.5487
RH | 4 | 10.2 | 422.9157 | 3160.9554 | _ | 6.2982 | 0.90803 | 586.9622
| 5 | 10.2 | 540 | 3473.7 | _ | 6.7142 | 0.90803 | 586.9622
CFWH5 | 6 | 8 | 496.9753 | 3390.7685 | _ | 6.7142 | 0.032207 | 20.819 | P6a= P6-P6(0.07) | P6a | 7.44 | T6a | 290.038 | h6a | 3433.0636
Deaerator | 7 | 5.8 | 442.9586 | 3287.5893 | _ | 6.7142 | 0.033135 | 21.4186 | P7a= P7-P7(0.07) | P7a | 5.394 | T7a | 268.7692 | h7a | 3361.7812
CFWH4 | 8 | 4.3 | 395.6944 | 3197.9236 | _ | 6.7142 | 0.0025683 | 1.6602 | P8a= P8-P8(0.07) | P8a | 3.999 | T8a | 250.3852 | h8a | 3281.491
CFWH3 | 9 | 4.2 | 392.095 | 3191.107 | _ | 6.7142 | 0.033825 | 21.865 | P9a= P9-P9(0.07) | P9a | 3.906 | T9a | 249 | h9a | 3237.2028
CFWH2 | 10 | 3 | 342.5326 | 3097.6024 | _ | 6.7142 | 0.0048682 | 3.1468 | P10a= P10-P10(0.07) | P10a | 2.79 | T10a | 229.902 | h10a | 3168.7986
CFWH1 | 11 | 2.8 | 332.8021 | 3079.3129 | _ | 6.7142 | 0.21961 | 141.9575 | P11a= P11-P11(0.07) | P11a | 2.604 | T11a | 226.1716 | h11a | 3124.9506
Cond. | 12 | 0.0055 | 34.58 | 2057.6146 | _ | 6.7142 | 0.58182 | 376.0951 | P12a= P12-P12(0.07) | P12a | 0.005115 | T12a | 32.974 | h12a | 2601.956
| 13 | 0.0055 | 34.58 | 144.95 | 1.0058 |  | 0.58182 | 376.0951
| 14 | h13+vf13(P14-P13) | 34.6686 | 147.7607 | _ |  | 0.58182 | 376.0951 | Assuming 500 MW
| 15 | hf at P11a | 226.1694 | 972.2296 | _ |  | 0.26087 | 168.6296 | m (kg/s) | 500MW/Wnet
| 16 | hf at T17 | 226.1716 | 972.2397 | _ |  | 0.26015 | 168.1626 | [6 empty] | 49552.8957 | 49.5529
| 17 | hf at T17 | 226.1716 | 972.2397 | _ |  | 0.58182 | 376.0951 | T17=T11a-TTD | 223.8716 |  |  |  |  | 29529.2252 | 29.5292
| 18 | hf at T17 | 226.1716 | 972.2397 | _ |  | 0.84269 | 544.7246 | [6 empty] | 46718.248 | 46.7182
| 19 | hf at P10a | 229.902 | 989.665 | _ |  | 0.041262 | 26.672 | [6 empty] | 23852.0468 | 23.852
| 20 | Tf at T20 | 229.902 | 978.9053 | _ |  | 0.84269 | 544.7246 | T20=T10a-TTD | 227.602 |  |  |  |  | 40356.0325 | 40.356
| 21 | hf at P9a | 249 | 1080.4856 | _ |  | 0.036393 | 23.5252 | [6 empty] | 43736.0612 | 43.7361
| 22 | Tf at T22 | 246.7 | 1069.404 | _ |  | 0.84269 | 544.7246 | T22=T9a-TTD | 246.7 |  |  |  |  | 24051.3257 | 24.0513
| 23 | hf at P8a | 250.3852 | 1087.2374 | _ |  | 0.0025683 | 1.6602 | [6 empty] | 35652.2475 | 35.6522
| 24 | Tf at T24 | 248.0852 | 1076.0915 | _ |  | 0.84269 | 544.7246 | T24=T8a-TTD | 248.0852 |  |  |  |  | 22715.5767 | 22.7156
| 25 | hf at P7a | 268.7692 | 1178.2976 | 1.2989 |  | 0.033135 | 21.4186 | [6 empty] | 196695.7022 | 196.6957
| 26 | h25+vf25(P26-P25) | 272.542 | 1194.6118 |  |  | 1 | 646.4122 | [7 empty] | 512.8594
| 27 | hf at P6a | 290.038 | 1289.262 | _ |  | 0.12418 | 80.2689
| 28 | hf at T28 | 287.738 | 1276.9083 | _ |  | 1 | 646.4122 | T28=T6a-TTD | 287.738
| 29 | hf at P3a | 315.3939 | 1433.3444 | _ |  | 0.091969 | 59.4499
| 30 | hf at T30 | 313.0939 | 1419.5634 | _ |  | 1 | 646.4122 | T30=T3a-TTD | 313.0939
| 31 | hf at P2a | 319.23 | 1456.74 | _ |  | 0.013203 | 8.5347
| 32 | hf at T32 | 316.93 | 1442.673 | _ |  | 1 | 646.4122 | T32=T2a-TTD | 316.93
|  | Mass Balance | Equation
|  | m1 | m1=(h32-h30)/(h2a-h31) | [6 empty] | m1+m2 | 0.091969
|  | m2 | m2=(1(h30-h28)+m1(h29-h31))/(h3a-h29) | [6 empty] | m1+m2+m3 | 0.12418
|  | m3 | m3=(m26(h28-h26)+m29(h27-h29))/(h6a-h27) | [6 empty] | 1-m1-m2-m3-m4 |  | 0.84269
|  | m4 | m4(h7a-h25)+(m1+m2+m3)(h27-h25)=(1-m1-m2-m3-m4)(h25-h24) | [6 empty] | m1+m2+m3+m4+m5 |  | 0.15988
|  | m5 | m5(h8a-h23)=m22(h24-h22) | [6 empty] | m1+m2+m3+m4+m5+m6 |  | 0.1937
|  | m6 | m6(h9a-h21)+m5(h23-h21)=(1-m1-m2-m3-m4-m5-m6)(h22-h20) | [6 empty] | m5+m6 |  | 0.036393
|  | m7 | m7(h10a-h19)+m21(h21-h19)=(1-m1-m2-m3-m4-m5-m6-m7)(h20-h18) | [6 empty] | m1+m2+m3+m4+m5+m6+m7 |  | 0.19465
|  | m8 | m8(h11a-h15)+m19(h19-h15)=(1-m1-m2-m3-m4-m5-m6-m7-m8)(h17-h14) | [6 empty] | m5+m6+m7 |  | 0.03734
|  | m1 | 0.013203
|  | m2 | 0.078766
|  | m3 | 0.032207
|  | m4 | 0.033135
|  | m5 | 0.0025683
|  | m6 | 0.033825
|  | m7 | 0.00094666
|  | m8 | 0.22281
|  | Qa=Qboiler+Qreheater |  |  | Eff | 0.35082
|  | Qboiler | 1920.827
|  | Qreheater | 283.9817
|  | Qa | 2204.8087
|  | Qr | 1431.3084
|  | Wnet | 773.5003

## List of Tables
LIST OF TABLES
Table No. | Title | Page No.
1 | Comparison of Parameters of the Three Locations
2 | Projected Load in MW from 2020-2030
3 | Ambient Condition in Brgy. Lumaniag, Lian,
Batangas
4 | Summary of Calculation for Design Option 1
5 | Summary of Calculation for Design Option 2
6 | Summary of Calculation for Design Option 3
7 | Summary of Calculation for the Three Design
Options
8 | Equipment Selection
9 | Comparison of Given Equipment
10 | Summary of Equipment
11 | Actual and Forecast Demand
12 | 2018 Electric Generation and Consumption in
MWh
13 | 2018 Monthly System Peak Demand in MW
14 | 2018 Power Generation by Source in GWh
15 | 2018 Summary of Power Generation by Grid in
GWh
16 | Region IV-A Peak Demand
17 | Project Costing Summary
18 | Depreciation Costs
19 | Return of Investment
20 | Payback Period
LIST OF FIGURES
Figure No. | Title | Page No.
1 | Organizational Chart
2 | Proposed Location of the Coal-Fired Power Plant
3 | Plant Location and Target Municipalities
4 | Schematic Diagram of Design Option 1
5 | T-S Diagram of Design Option 1
6 | Schematic Diagram of Design Option 2
7 | T-S Diagram of Design Option 2
8 | Schematic Diagram of Design Option 3
9 | T-S Diagram of Design Option 3
10 | STF Turbine, GE
11 | Two-Pass Boiler, GE
12 | Condenser, GE
13 | SPX Heater, Energyen
14 | Deaerator, Eurowater
15 | Boiler Feedwater Pump, FLOWSERVE
16 | Condensate Extraction Pump, FLOWSERVE
17 | Circulating Water Pump, FLOWSERVE
18 | Steam Trap, EMERSON
19 | Water Cooled Generator, GIGATOP
20 | Transport System
21 | Water Treatment System Diagram
22 | Batangas II Electric Cooperative Inc.
(BATELEC II) Supply-Demand